| 10 | 1 | PRIODOOR ETX RDA Smoke damper – according to EN 12101-8 Large-size, single-vent, fire resistant, specially designed for installation in RDA outlet ducts (RDA = Smoke protection pressure systems). The aim of the application is to keep safety staircases smokefree. When a fire occurs, the exhaust damper is automatically opened by the control unit of the RDA supplied by the customer. Large-size cross sections offer a free unhindered outlet surface area for combustion gases. The closure is smoke-proof and offers fire resistance for up to 90 minutes. Function: Tested as a smoke damper Fire resistance 90 minutes Classification EI 90 (Ved – i ↔o) S500C10000 AAmulti Smoke protection Tight seal Pressure / suction stable up to 500 Pa Sound reduction index depending on size up to 36 dB Construction: Single panel shaft closing with high mechanical durability Flush-fitting assembly in solid shaft walls with assembly frames Free large format flow surface External construction height from 1150 mm to 2500 mm, depending on wall systems External construction width from 500 mm to 1,000 mm Folded block frame: three sided 64 mm, locking side 139 mm All round smoke and fire protection seals, automatically foams in the event of fire High-quality stainless steel bands When installed in a solid wall ≥ 110 mm thick, it is possible to retrofit the door leaf with a cladding of up to 11 kg/m² made of non-combustible material. Subsequent, on-site painting of the smoke damper on the outside is possible. Drive: Opened and closed by chain drive System voltage 24 V DC Power consumption 40 mA, max. 1 A in cut-out torque With integrated adjustable limit switch; standard: „End position“ open Lock with power cut-off Chain drive adjusted by software Connector cable chain drive 6-pole, 3.00 m (2 conductors each for drive, limit and programming) Material characteristic: Non-combustible board with surface coating, classification A2 - s1, d0 Standard CPL surface Standard color light grey - similar to RAL 7035, colored edges and chamfers Green Building Declaration according to LEED and DGNB Scope of delivery: Smoke damper Assembly frame Chain drive with connector cable (3.00 m) Attachment material Options: Chain drive with special chain lengths Commissioning set Standardised colours - white, similar to RAL 9016; decor brushed aluminium; primer foil Special decors / special colours Protective plate for smoke extraction flap Element-external dimensions (H x B) in mm: ………………………………….. Rough opening (H x B) in mm: ………………………………….. Surface: ………………………………….. Typ: PRIODOOR ETX RDA Fabrikat: PRIORIT AG www.priorit.de Tel.: +49 6181 3640-0 Fax : +49 6181 3640-230 |  |  |
| --- | --- | --- | --- | --- |