| 10 | 1 | PRIOAIR SD-RDA-V Smoke extraction damper for use in smoke protection pressure systems according to EN 12101-8 Large-format, single-leaf, fire-resistant smoke damper, specially designed to seal off outflow shafts as part of a smoke pressure system. The goal of using these is to keep safety stairwells free from smoke. In case of a fire, the controller of the on-site smoke pressure system opens the smoke damper automatically. Large cross-sections offer a free, unimpeded outflow area for flue gases. The closure is smoke proof and offers a fire resistance rating of over 90 minutes. PRIOAIR SD-RDA-V is classified for vertical installation in walls and ducts and thus has the classification vedw (d = duct smoke extraction duct, w = wall, wall - part of the smoke extraction duct) required for installation in shaft walls and offers an outflow area of up to 1.74 m² at pressure stage 2 in the largest dimension. Function Performance level according to MVV TB 2023/1: EI90(vedw i<->o)S1000C10000 Smoke extraction damper according to EN12101-8 Fire resistance 90 minutes EI90 Fire from inside, fire from outside Pressure suction – pressure stage 2 1000 Pa Automatic motorised release AA Smoke protection – circumferential fire and smoke protection seals Tight seal Installation and assembly Vertical, flush installation in solid walls for smoke extraction, also in connection with smoke extraction ducts according to EN 12101-7, tested according to EN 1366-8 or EN 1366-9 Flush installation in PRIOWALL and GKF shaft wall Installation in duct / vertical line Raised installation Mounting frame included Opening and closing Large free outflow area in relation to the installation opening Opening and closing via high-quality chain drive Emergency release Easy unlocking of the cover frame (standard version with screw connection) Large opening angle (75°) Quick opening and closing of the smoke control damper, Speed approx. 10 mm/sec. Opening after approx. 35 seconds Pressure loss coefficients ζ determined by the Institute for Industrial Aerodynamics (I.F.I.) and available on request Drive Bolt drive for additional locking (multi-point locking) Opening and closing by chain drive Connection cable chain drive 6-pole, (2 wire pairs each for drive, end positions and programming) System voltage 24 V DC Adjustment of the chain drive via software Automatic reversing in case of overload (reversal of the direction of movement when an obstacle is detected) Material & Surface Standard surface light grey, similar to RAL 7035, edges and chamfers dark Different surface designs - from décor to primer film, paint Surface can be plastered over/coated according to manufacturer‘s instructions Look No visible bands from the corridor side No visible drive from the corridor side One-piece frame cover without joints Optionally with suspended frame cover (without visible screw connection) Quality Declaration according to DGNB, LEED and BNB Production exclusively “Made in Germany” All tests by renowned test institutes within Germany Sizes Single-leaf manhole cover Nominal sizes from 620 x 1050 mm to 1000 x 2500 mm (W x H) Options Special version without visible screws Surface: ………………………………….. Options: ………………………………….. ………………………………….. Typ: PRIOAIR SD-RDA-V Fabrikat: PRIORIT AG www.priorit.de Tel.: +49 6181 / 3640 0 Fax : +49 6181 / 3640 210 |  |  |
| --- | --- | --- | --- | --- |