| 10 | 1 | PRIOELEC ESL – 30 Minutes Free-Standing Electrical Cabinets PRIORIT free-standing electrical cabinets in single- and double-leaf design, suitable for a smoketight and fire-resistant separation of electrical distributors in escape and rescue routes (fire load insulation). The housing is made of non-combustible building material class A2 – s1 d0. As standard, cabinets are equipped with a ventilation system in the rear wall, top and bottom cable entry. The inside dimensions are based on the standard distribution panels and mounting plates. Function Fire resistance of 30 min, fire-retardant Suitable for fire load insulation of 30 minutes Smoke protection, cold smoke-proof Empty housing tested and certified by the VDE testing institute according to DIN EN 62208 Protection class: IK10, IP 44 Protection class II CE marking Construction Empty housing with high mechanical resistance Door hinges made from stainless steel Door can be unhinged Door hinge can be changed on site Door integrated into body, opening angle approx. 180° 2-point door lock via pivot lever with double-bit cylinder (can be replaced with home locking system) Circumferential fire protection seal, foams automatically in case of fire Cable feed top + bottom for bundle insertion Fixing rails for installation of device support brackets or mounting plate Tilt safe-guard for housing through fixing lugs at top Integrated base, can be driven under, with removal front panel Material characteristic Non-combustible board with surface coating, classification A2 – s1, d0 Standard CPL surface Colour light grey, similar to RAL 7035, edges and bevels in different colour Scope of delivery Empty enclosure, with integrated thermal fuse Options Standardised colours - white, similar to RAL 9016; decor brushed aluminium; primer foil Special decors / special colours Additional rear panel for free housing installation Ventilation system, consisting of fan and smoke detector, ready for connection (230 V AC) Ventilation system, consisting of fan and smoke detector, ready for connection (24 V DC) Notice If the fan unit is retrofitted, the usable height is reduced by one height unit. Element-External dimension (H x B x T) in mm: ………………………………….. Surface: ………………………………….. Weight: ………………………………….. Door hinge (DIN L / DIN R): ………………………………….. Panel height: ………………………………….. Panel width: ………………………………….. Unit space: ………………………………….. Options: ………………………………….. Typ: PRIOELEC ESL30 Fabrikat: PRIORIT AG www.priorit.de Tel.: +49 6181 3640-0 Fax : +49 6181 3640-230 |  |  |
| --- | --- | --- | --- | --- |