| 10 | 1 | PRIORIT HSRZ CONT Mobile high-security room cell in container format PRIORIT HS-RZ CONT is a fire-resistant IT-Room for the protection of IT, communication and network systems to EN 1047-2. As a flexibly usable and easy to transport container space solution, the standard HS-RZ CONT is prepared for flexible customer use and individual customer equipping with IT components. The space solution fulfils the strict requirements of EN 1047-2 and is ECB-S certified. Function Fire resistance 180 minutes (Element testing for wall, ceiling, floor) Fire resistance 90 minutes (Element testing for doors, penetration seals) R 60 D classification Compliance with the limits specified in EN 1047 Part 2 ECB•S certification System test by official material testing institute Protection rating according to IP 56 Anti-burglary protection according to RC2 DIN EN 1627 Construction Standard ISO shipping container as external housing Wall structure inside made of autoclaved aerated concrete (AAC) (PP2 0.4 Thermal conductivity coefficient = 0.11 W/mK, 240 mm thick) Solid construction floor and ceiling elements inside (PDE4.4 0.55 Thermal conductivity coefficient = 0.18 W/mK, 250 mm thick) Additional internal lining with aluminum vapor barrier as protection against electromagnetic radiation and moisture Fire door Roxtec cable penetration seal with maintenance door Material characteristic Steel sheet, painted outside Standard colour white resembling RAL 9016 Options Cladding of the container for outdoor installation Individual internal paneling Access control system Rail system, individually projectable, for simple installation and long-term IT-rack mobility Additional ‘Roxtec’ cable sealing with maintenance door Room external dimension (H x B x T) in mm: ………………………………….. Numbers of doors: ………………………………….. Numbers of cable and pipe bulkheads: ………………………………….. Individual out site paneling: ………………………………….. Typ: PRIORIT HSRZ CONT Fabrikat: PRIORIT AG www.priorit.de Tel.: 06181 / 3640 0 Fax : 06181 / 3640 230 |  |  |
| --- | --- | --- | --- | --- |