| 10 | 1 | PRIODOOR NK TUN Emergency telephone box door Emergency phone boxes made of concrete elements provided by the customer. Designed according to Directive 2004/54/EG, RABT, ZTV-ING Part 5 and TL/TP TTT. The design considers the special requirements for technical equipment used in the operation of road tunnels, and is suitable as a fire protection closure for the maintenance of performance of electrical security systems. Function Fire resistance 90 minutes: fire-resistant T 90-RS classification Smoke-tight and tested for continuous operation Protection rating in accordance with IP 54 Stable against pressure / suction up to 1000 Pa Safety class I Construction Single-leaf fire-resisting closure with block frame Solid door leaf with stainless steel surface on the outside F 90 glass up to max. 45% of the door area Adjustable stainless steel hinges and multiple bolt lock Self-closing door with cushioned pinion door closers EN-standard door handle set in stainless steel Identification with pictograms according to RABT Monitorable door status by inductive proximity switch, 90° rotatable Equipotential bonding Material characteristic Building material A2 – s1, d0 non-combustible Building material is chemically highly stable, solid, stable and moisture-resistant Surface on one side (outside) in stainless steel 1.4571, material characteristic according to ZTV-ING Part 5, requirement class I, Surface on the hinge side powder coated, RAL 2009 Traffic Orange Strike plates in stainless steel 1.4571 Lieferumfang Door PRIODOOR NK TUN Installation Instruction Optionen Special sizes on request Element-External dimension (H x B) in mm: ………………………………… Rough opening (H x B) in mm: ………………………………….. Surface: ………………………………….. Weight: ………………………………….. Wall type: ………………………………….. Door stop (DIN L / DIN R): ………………………………….. Dimension glas elements (H x B) in mm: ………………………………….. Options: ………………………………….. Typ: PRIODOOR NK TUN Fabrikat: PRIORIT AG www.priorit.de Tel.: 06181 / 3640 0 Fax : 06181 / 3640 230 |  |  |
| --- | --- | --- | --- | --- |