| 10 | 1 | PRIOELEC EK TUN Tunnel Electro Terminal Box without Equipment Terminal box as empty case for the installation of electric connections and safety fuses. This double-ply casing is designed specifically to guarantee the maintenance of performance function of safety-relevant electrical systems in road tunnels according to RABT and for the star-shaped wiring, connection and fusing electrical installations required for the maintenance of performance. Design according to DIN 4102, Directive 2004/54/EG, RABT, ZTV-ING Part 5. Function Fire resistance 90 minutes: fire-resistant Classification: Suitable for the maintenance of performance of electrical installations up to 90 minutes. Fire chamber test, according to EN 1363-1 Safety class II Protection rating in accordance with IP 65 Stable against pressure / suction up to 1000 Pa Construction of inner casing Fixed to outer casing by 4 bolted connections Cover with recessed grip and bolted down with self-locking nuts Mounting of installations via pre-drilled holes in grid dimension Cable entry from two opposite sides Cable compartments automatically expand in the event of a fire Construction of outer casing Stainless steel casing 1.4571 for mounting to a solid wall or solid ceiling Fastening to outside mounting brackets via four enclosed anchor bolts made of stainless steel 1.4529 Casing cover easy to remove, eightfold bolting Cable entry on 2 sides via plastic M-screw-connections according to ZTV-ING Part 5 and RABT Material characteristic inner casing Building material with surface coating, classified A2 – s1, d0 non-combustible Building material has a high chemical stability, mechanical strength and stability Metal parts made of stainless steel 1.4571 Material characteristic outer casing Metal casing made of stainless steel 1.4571 Cable tie mount made of stainless steel 1.4529 Cable entries made of plastic according to ZTV-ING Part 5 and RABT Scope of delivery Stainless steel casing including inner casing, mounting hardware for wall mounting and ceiling suspension Element-External dimension (H x B x T) in mm: ………………………………….. Weight: ………………………………….. Cable entry: ………………………………….. Options: ………………………………….. Typ: PRIOELEC EK TUN Fabrikat: PRIORIT AG www.priorit.de Tel.: 06181 / 3640 0 Fax : 06181 / 3640 230 |  |  |
| --- | --- | --- | --- | --- |